## Instructions
Instructions for Spreadsheet Calculations for the Potential to Emit from Stationary Internal Combustion Engines
These spreadsheets are designed to help you determine the potential to emit from gasoline and diesel internal combustion engines using distillate oil, dual fuel, natural gas, or unleaded gasoline.
Step 1
Choose one of the worksheets to calculate your emissions. Worksheet 1 calculates emissions based on horsepower-hour and Worksheet 2 calculates emissions based maximum fuel usage/hr and calculates this to million BTU/hr.
Step 2
Each of the worksheets has multiple tables with emission factors based on the type of unit you operate. Use the table that corresponds to the type of fuel used and horsepower potential (listed at the top of each table):
| Table 1 | Distillate Oil (Sulfur 0.5%) | < 600 hp
| Table 2 | Distillate Oil (Sulfur 0.5%) | > 600 hp
| Table 3 | Dual Fuel
| Table 4 (only on fuel page) | Natural Gas
| Table 4 (or Table 5 on fuel input worksheet) | Unleaded Gasoline | < 250 hp
Step 3
Enter the power output (in hp) or maximum hourly fuel usage (in gallons for diesel and gasoline and standard cubic foot for natural gas) in the corresponding highlighted field within the appropriate table as determined above. All tables refering to diesel assume .5% sulfur content. If you are required to use a fuel with a lesser sulfur content, alter the corresponding sulfur content field for Tables 1 or 2 of Worksheet 1. For dual fuel engines, enter the maximum million BTU per hour the unit can burn per the manufacturer's specifications. The potential emissions will then be automatically calculated.
The calculations are based upon 8,760 hours of operation. If you have an air quality permit that limits your hours of operation, you will have to change the equation in the Emissions (ton/yr) column to reflect that limit. Please note you will have to calculate the emissions for each engine and sum the emissions for each pollutant. This spreadsheet is only set up to calculate one engine’s emissions per table.
Note: The emission factors used in this spreadsheet are generally assumed to be representative of long-term average emission rates and may not accurately represent emissions at your particular facility. The use of more representative emission factors obtained from stack tests or continuous monitoring systems (CEMS) is recommended when available. Contact the Air Quality Division if you have questions regarding the suitability of emission factors for your particular source.
Step 4
Save a copy of your maximum potential emission calculations electronically and as a printout. If you need to apply for a permit, please submit a copy of your calculations with your permit application. Please note that if your operations change, you will have to reevaluate if you need an air quality permit. If you have any questions, please call the Air Quality Division at (877) 834-0474 or (402) 471-2189.

## Wksht 1-hp-hr
For help call the NDEQ
1(877)834-0474 or (402)471-2189
TABLE 1 - Diesel Engine-driven Generators, < 600 hp
Fuel: Diesel |  |  | Engine Output: | 447
Sulfur Content (%) = | 0.5 |  | Electrical Output[1]: | 300.1158
Heat Content (Btu/gal) = | 137000 |  | Max. Fuel Input[2]: | 22.8394
Pollutant |  | Emission Factor | E.F. Unit | Emission Factor Source[3] | Emission Rate (lb/hr) | Emissions (ton/yr)
PM |  | 0.0022 | lb/hp-hr | Table 3.3-1 | 0.9834 | 4.3073
PM10 |  | 0.0022 | lb/hp-hr | Table 3.3-1 | 0.9834 | 4.3073
SOx |  | 0.00205 | lb/hp-hr | Table 3.3-1 | 0.91635 | 4.0136
NOx |  | 0.031 | lb/hp-hr | Table 3.3-1 | 13.857 | 60.6937
CO |  | 0.00668 | lb/hp-hr | Table 3.3-1 | 2.986 | 13.0785
VOC[4] |  | 0.00247 | lb/hp-hr | Table 3.3-1 | 1.1041 | 4.8359
Individual HAP (formaldehyde) |  | 0.00118 | lb/MMBtu | Table 3.3-2 | 0.0036922 | 0.016172
Total HAPs |  | 0.00387 | lb/MMBtu | Table 3.3-2 | 0.012109 | 0.053038
[1] Applicable for electrical generator sets, estimated by the equation kW = (hp) * (0.746 kW/hp) * (90% effeciency)
[2] Estimated using an average Brake Specific Fuel Consumption (BSFC) of 7,000 Btu/hp-hr
[3] AP-42 Section 3.3 - Gasoline & Industrial Diesel Engines (10/96)
[4] VOC expressed as total organic compounds
TABLE 2 - Diesel Engines & Generators, > 600 hp
Fuel: Diesel |  |  | Engine Output: | 600
Sulfur Content (%) = | 0.5 |  | Electrical Output[1]: | 402.84
Heat Content (Btu/gal) = | 137000 |  | Max. Fuel Input[2]: | 30.6569
Pollutant |  | Emission Factor | E.F. Unit | Emission Factor Source[3] | Emission Rate (lb/hr) | Emissions (ton/yr)
PM |  | 0.0007 | lb/hp-hr | Table 3.4-1 | 0.42 | 1.8396
PM10 |  | 0.0007 | lb/hp-hr | Table 3.4-1 | 0.42 | 1.8396
SOx |  | 0.004045 | lb/hp-hr | Table 3.4-1 | 2.427 | 10.6303
NOx |  | 0.024 | lb/hp-hr | Table 3.4-1 | 14.4 | 63.072
CO |  | 0.0055 | lb/hp-hr | Table 3.4-1 | 3.3 | 14.454
VOC[4] |  | 0.00064155 | lb/hp-hr | Table 3.4-1 | 0.38493 | 1.686
Individual HAP (benzene) |  | 0.000776 | lb/MMBtu | Table 3.4-3 | 0.0032592 | 0.014275
Total HAPs |  | 0.00157 | lb/MMBtu | Table 3.4-3 | 0.006594 | 0.028882
[1] Applicable for electrical generator sets, estimated by the equation kW = (hp) * (0.746 kW/hp) * (90% effeciency)
[2] Estimated using an average Brake Specific Fuel Consumption (BSFC) of 7,000 Btu/hp-hr
[3] AP-42 Section 3.4 - Large Stationary Diesel & Dual Fuel Engines (10/96)
[4] VOC expressed as total non-methane organic compounds (91% ot TOC)
TABLE 3 - Dual Fuel Engine-driven Generators
Fuel: Dual Fuel |  |  | Power Output: |  | hp
Pollutant | Emission Factor (lb/hp·hr) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
Pma | 0.0007 | Table 3.4-1 | 0 |  | 0
PM10a | 0.0007 | Table 3.4-1 | 0 |  | 0
Soxb | 0.0002987 | Table 3.4-1 | 0 |  | 0
NOx | 0.018 | Table 3.4-1 | 0 |  | 0
CO | 0.0075 | Table 3.4-1 | 0 |  | 0
VOC c | 0.00132 | Table 3.4-1 | 0 |  | 0
Individual HAP (formaldehyde) | - | - | - |  | -
Total HAPs | - | - | - |  | -
a Used Diesel Fuel Values |  | AP-42 (10/96)
b Assuming Sulfur % = .5 in fuel oil and Sulfur % = .01 in natural gas
c Total non-methane VOCs
TABLE 4 - Gasoline Engine-Driven Generators, < 250 hp
Fuel: Unleaded Gasoline |  |  | Power Output: |  | hp
Pollutant | Emission Factor (lb/hp·hr) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
PM | 0.000721 | Table 3.3-1 | 0 |  | 0
PM10 | 0.000721 | Table 3.3-1 | 0 |  | 0
SOx | 0.000591 | Table 3.3-1 | 0 |  | 0
NOx | 0.011 | Table 3.3-1 | 0 |  | 0
CO | 0.439 | Table 3.3-1 | 0 |  | 0
VOC a | 0.015 | Table 3.3-1 | 0 |  | 0
Total HAPs | - | - | - |  | -
a Total non-methane VOCs |  | AP-42 (10/96)

## Wksht 2-fuel input
For help call the NDEQ
1(877)834-0474 or (402)471-2189
TABLE 1 - Diesel Engine-driven Generators, < 600 hp
Fuel: Diesel (Sulfur ≤ 0.5%) |  |  | Fuel Input: |  | MMBtu/hr
Pollutant | Emission Factor (lb/MMBtu) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
PM | 0.31 | Table 3.3-1 | 0 |  | 0
PM10 | 0.31 | Table 3.3-1 | 0 |  | 0
SOx | 0.29 | Table 3.3-1 | 0 |  | 0
NOx | 4.41 | Table 3.3-1 | 0 |  | 0
CO | 0.95 | Table 3.3-1 | 0 |  | 0
VOC a | 0.35 | Table 3.3-1 | 0 |  | 0
Individual HAP (formaldehyde) | 0.00118 | Table 3.3-2 | 0 |  | 0
Total HAPs | 0.00379 | Table 3.3-2 | 0 |  | 0
a Total non-methane VOCs |  | AP-42 (10/96)
TABLE 2 - Diesel Engine-driven Generators, > 600 hp
Fuel: Diesel (Sulfur ≤ 0.5%) |  |  | Fuel Input: |  | MMBtu/hr
Pollutant | Emission Factor (lb/MMBtu) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
PM | 0.0697 | Table 3.4-2 | 0 |  | 0
PM10 | 0.0573 | Table 3.4-2 | 0 |  | 0
SOx | 0.505 | Table 3.4-1 | 0 |  | 0
NOx | 3.2 | Table 3.4-1 | 0 |  | 0
CO | 0.85 | Table 3.4-1 | 0 |  | 0
VOC a | 0.0819 | Table 3.4-1 | 0 |  | 0
Individual HAP (benzene) | 0.000776 | Table 3.4-3 | 0 |  | 0
Total HAPs | 0.00157 | Table 3.4-3 | 0 |  | 0
a Total non-methane VOCs |  | AP-42 (10/96)
TABLE 3 - Dual Fuel Engine-driven Generators
Fuel: Dual Fuel |  |  | Fuel Input: |  | MMBtu/hr
Pollutant | Emission Factor (lb/MMBtu) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
Pma | 0.0697 | Table 3.4-2 | 0 |  | 0
PM10a | 0.0573 | Table 3.4-2 | 0 |  | 0
Soxb | 0.03395 | Table 3.4-1 | 0 |  | 0
NOx | 2.7 | Table 3.4-1 | 0 |  | 0
CO | 1.16 | Table 3.4-1 | 0 |  | 0
VOC c | 0.2 | Table 3.4-1 | 0 |  | 0
Individual HAPa (benzene) | 0.000776 | Table 3.4-3 | 0 |  | 0
Total HAPsa | 0.00157 | Table 3.4-3 | 0 |  | 0
a Used Diesel Fuel Values |  | AP-42 (10/96)
b Assuming Sulfur % = .5 in fuel oil and Sulfur % = .01 in natural gas
c Total non-methane VOCs
TABLE 4 - Natural Gas Engine-Driven Generators
Fuel: Natural Gas |  |  | Fuel Input: | 1000 | scf/hr
|  |  |  | 1.02 | MMBtu/hr
Pollutant | Emission Factor (lb/MMBtu) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
PM | 0.0483 | Table 3.2-1 | 0.049266 |  | 0.21579
PM10 | 0.048 | Table 3.2-1 | 0.04896 |  | 0.21444
SOx | 0.000588 | Table 3.2-1 | 0.00059976 |  | 0.0026269
NOx | 4.08 | Table 3.2-2 | 4.1616 |  | 18.2278
CO | 3.72 | Table 3.2-3 | 3.7944 |  | 16.6195
VOC | 0.12 | Table 3.2-1 | 0.1224 |  | 0.53611
Individual HAP (formaldehyde) | 0.055 | Table 3.2-1 | 0.0561 |  | 0.24572
Total HAPs | 0.08 | Table 3.2-1 | 0.0816 |  | 0.35741
Using worst-case emission factors from AP-42 Tables for 2-stroke LB, 4-stroke LB, and 4-stroke RB (07/00)
TABLE 5 - Gasoline Engine-Driven Generators, < 250 hp
Fuel: Unleaded Gasoline |  |  | Fuel Input: |  | gallons/hr
|  |  |  | 0 | MMBtu/hr
Pollutant | Emission Factor (lb/MMBtu) | Emission Factor Source | Emission Rate (lb/hr) |  | Emissions (ton/yr)
PM | 0.1 | Table 3.3-1 | 0 |  | 0
PM10 | 0.1 | Table 3.3-1 | 0 |  | 0
SOx | 0.084 | Table 3.3-1 | 0 |  | 0
NOx | 1.63 | Table 3.3-1 | 0 |  | 0
CO | 62.7 | Table 3.3-1 | 0 |  | 0
VOC a | 2.1 | Table 3.3-1 | 0 |  | 0
Total HAPs |  |  | n/a |  | n/a
a Total non-methane VOCs |  | AP-42 (10/96)